SITE ACCEPTANCE TEST REPORT

Water for Injection Storage and Distribution System

SAT-WFI-001-R  ·  REVISION 0.1

| Project reference | PRJ-2026-0009 |
| --- | --- |
| Equipment reference | EQ-02 — WFI Storage and Distribution System |
| Document status | Draft |
| Records execution of | SAT-WFI-001 Rev 0.1 |
| Site | [Site name and location] |
| Supplier | [Supplier name] |
| Test dates | [DD-MMM-YYYY] to [DD-MMM-YYYY] |
| Prepared by | [Enter author] |

This report records the results of the tests defined in SAT-WFI-001 as observed at site. Acceptance criteria are reproduced from the approved protocol without amendment. Results were recorded by the persons named against each test and are reproduced without alteration. This report has no validity until reviewed and approved in accordance with the site quality system. Pharma4i does not perform or record document approval.

# Related Documents

| Document | Number | Rev | Status | Relationship |
| --- | --- | --- | --- | --- |
| User Requirements Specification | URS-WFI-001 | 0.1 | Issued | Source of requirements |
| Design Qualification | DQ-WFI-001 | 0.1 | Issued | Source of open observations |
| FAT Protocol | FAT-WFI-001 | 0.1 | Issued | Preceding test |
| FAT Report | FAT-WFI-001-R | 0.1 | Issued | Source of deferrals, deviations and punch list |
| SAT Protocol | SAT-WFI-001 | 0.1 | Draft | This protocol |
| SAT Report | SAT-WFI-001-R | 0.1 | Draft | Records execution of this protocol |
| Installation Qualification | IQ-WFI-001 | — | Planned | Receives requirements outstanding after SAT |
| Operational Qualification | OQ-WFI-001 | — | Planned | Planned |
| Performance Qualification | PQ-WFI-001 | — | Planned | Planned |
| Validation Summary Report | VSR-WFI-001 | — | Planned | Planned |

# Table of Contents

# 1. Introduction

This report records the execution of SAT-WFI-001 Revision 0.1 at site. It reproduces the acceptance criteria from the approved protocol without amendment, records the result observed against each, and lists every deviation raised.

No acceptance criterion was amended during execution. Where a criterion could not be applied because URS-WFI-001 does not fix a value, the test is recorded as not executed and the finding is against the specification.

# 2. Summary of Results

| Outcome | Count | Note |
| --- | --- | --- |
| Pass | 19 |  |
| Fail | 19 | Each raised as a deviation; see Section 8. |
| Not executed | 1 | Acceptance criterion not defined in the specification. |

Tests defined in the protocol: 39 (15 installation, 24 functional).

## 2.1 Deviations raised at Site Acceptance

| Classification | Count | Effect |
| --- | --- | --- |
| Critical | 4 | Prevents progression to Operational Qualification until closed and retested. |
| Major | 7 | Prevents progression unless a concession is approved by Quality Assurance. |
| Minor | 7 | May be carried with an agreed closure date. |

## 2.2 Critical deviations

- SDEV-001 (SAT-I-07) — Three branches exceed the 3D dead leg limit: one reworked skid branch at 3.4D and two site-installed branches at 3.6D and 4.1D.

- SDEV-003 (SAT-I-06) — The branch serving POU-07 retains water after draining.

- SDEV-009 (SAT-I-13) — No temperature mapping ports installed at the worst-case locations listed in the URS worst-case register.

- SDEV-017 (SAT-F-21) — No point-of-use coolers installed. Four points of use require water below loop temperature and cannot be served as specified.

## 2.3 Factory Acceptance deviation closure

12 of 14 Factory Acceptance deviations were closed at Site Acceptance. 2 remain open.

- DEV-001 remains open — Eight of nine reworked branches now at or below 3D; one at 3.4D. Two site-installed branches also exceed 3D.

- DEV-011 remains open — Completion logic corrected, but acceptance values remain undefined in URS-014.

## 2.4 Requirements deferred from Factory Acceptance

18 of the 36 requirements deferred from Factory Acceptance were verified at Site Acceptance. 16 were deferred again to Operational or Performance Qualification, and the remainder could not be executed because the specification does not fix a value. Full disposition at Section 6.

# 3. Installation Verification Results

SAT-I-01 — Verify the equipment arrived undamaged and complete against the shipping record.

| Test ID | SAT-I-01 |
| --- | --- |
| Traces to | Installation verification |
| Objective | Verify the equipment arrived undamaged and complete against the shipping record. |

Method

1. Compare the delivered items against the packing list and shipping condition record.

2. Inspect all surfaces, connections and instruments for transit damage.

3. Confirm shock and tilt indicators, where fitted, have not been triggered.

Acceptance criterion

All items delivered, no transit damage, no triggered transit indicators.

| Test instrument | — | Result | All items present. No damage. Tilt indicators intact. |  |
| --- | --- | --- | --- | --- |
| Performed by |  | Pass / Fail | Pass | Date |

SAT-I-02 — Verify location, orientation and access against the site layout.

| Test ID | SAT-I-02 |
| --- | --- |
| Traces to | Installation verification |
| Objective | Verify location, orientation and access against the site layout. |

Method

1. Compare installed position against the general arrangement and site layout drawing.

2. Confirm maintenance access and instrument access clearances.

Acceptance criterion

Installed position matches the layout drawing. Access clearances as drawn.

| Test instrument | Tape measure | Result | Position correct. Clearance to the east wall is 640 mm against 750 mm drawn. |  |
| --- | --- | --- | --- | --- |
| Performed by |  | Pass / Fail | Fail | Date |

Comment: Access to the heat exchanger head is restricted. SDEV-004.

SAT-I-03 — Verify levelling, anchoring and support.

| Test ID | SAT-I-03 |
| --- | --- |
| Traces to | Installation verification |
| Objective | Verify levelling, anchoring and support. |

Method

1. Check the skid is level to its installed datum.

2. Confirm all anchor bolts are fitted and torqued to the stated value.

3. Confirm pipe supports are installed at the intervals shown on the isometrics.

Acceptance criterion

Skid level within supplier tolerance. All anchors fitted and torqued. Supports at drawn intervals.

| Test instrument | Digital level, torque wrench | Result | Level within tolerance. All 12 anchors torqued. Two supports missing on the north riser. |  |
| --- | --- | --- | --- | --- |
| Performed by |  | Pass / Fail | Fail | Date |

Comment: SDEV-005, minor. Punch item.

SAT-I-04 — Verify utility connections against the utility schedule.

| Test ID | SAT-I-04 |
| --- | --- |
| Traces to | URS-036 |
| Objective | Verify utility connections against the utility schedule. |

Method

1. For each utility, confirm the connection is made at the stated point.

2. Record supply pressure, temperature and quality at each connection.

3. Confirm isolation and drain provision at each connection.

Acceptance criterion

ACCEPTANCE CRITERION NOT DEFINED IN THE URS. URS-036 leaves the utility envelope as [TO BE CONFIRMED].

| Test instrument | Calibrated gauges | Result | All six utilities connected. Heating medium supplied at 4.2 barg, 145 degrees C. Compressed air at 6.1 barg. |  |
| --- | --- | --- | --- | --- |
| Performed by |  | Pass / Fail | Not executed | Date |

Comment: No specified envelope to verify against. Values recorded for information. Finding against the specification.

SAT-I-05 — Verify slope of site-installed pipework.

| Test ID | SAT-I-05 |
| --- | --- |
| Traces to | URS-039 |
| Objective | Verify slope of site-installed pipework. |

Method

1. Measure fall on every horizontal run of site-installed pipework.

2. Record fall as a ratio against the drawn value.

Acceptance criterion

Continuous fall of not less than 1 in 100 towards designated drain points on all site-installed pipework.

| Test instrument | Digital level, accuracy 0.1 degrees or better | Result | 19 runs measured. 17 at 1:95 or better. Two runs in the north bay at 1:130. |  |
| --- | --- | --- | --- | --- |
| Performed by |  | Pass / Fail | Fail | Date |

Comment: SDEV-002.

SAT-I-06 — Verify drainability of the complete installed system.

| Test ID | SAT-I-06 |
| --- | --- |
| Traces to | URS-048 |
| Objective | Verify drainability of the complete installed system. |

Method

1. Fill the complete system with water.

2. Open all drain points and allow to drain for 30 minutes.

3. Inspect all low points, branches and points of use for retained water.

Acceptance criterion

No retained water anywhere in the installed system.

| Test instrument | Boroscope | Result | Retained water in one branch serving point of use POU-07. |  |
| --- | --- | --- | --- | --- |
| Performed by |  | Pass / Fail | Fail | Date |

Comment: SDEV-003, critical. Same defect class as FAT DEV-002 but on site pipework.

SAT-I-07 — Verify dead leg dimensions on the complete installed system, including reworked skid branches.

| Test ID | SAT-I-07 |
| --- | --- |
| Traces to | URS-047 ¦ Closes FAT DEV-001 |
| Objective | Verify dead leg dimensions on the complete installed system, including reworked skid branches. |

Method

1. Measure every branch on the installed system from the internal wall of the main loop to the point of closure.

2. Express as a multiple of internal pipe diameter.

3. Record every branch, distinguishing reworked skid branches from site-installed branches.

Acceptance criterion

No dead leg exceeds three internal pipe diameters (3D) as required by URS-047.

| Test instrument | Calibrated rule / calipers | Result | 31 branches measured. Eight of the nine reworked skid branches now at or below 3D; one at 3.4D. Two site-installed branches at 3.6D and 4.1D. |  |
| --- | --- | --- | --- | --- |
| Performed by |  | Pass / Fail | Fail | Date |

Comment: FAT DEV-001 partially closed. Three branches remain above 3D. SDEV-001.

SAT-I-08 — Verify passivation of the complete system.

| Test ID | SAT-I-08 |
| --- | --- |
| Traces to | URS-043 |
| Objective | Verify passivation of the complete system. |

Method

1. Obtain the passivation certificate and procedure record.

2. Confirm the scope of passivation covers the complete installed system.

3. Confirm the final rinse water quality record.

Acceptance criterion

Passivation performed on the complete installed system to a documented procedure, with certificate and final rinse record.

| Test instrument | — | Result | Certificate issued. Scope covers the skid only. Site-installed pipework was not included. |  |
| --- | --- | --- | --- | --- |
| Performed by |  | Pass / Fail | Fail | Date |

Comment: SDEV-006, major.

SAT-I-09 — Verify cleanliness of the installed system before commissioning.

| Test ID | SAT-I-09 |
| --- | --- |
| Traces to | Installation verification |
| Objective | Verify cleanliness of the installed system before commissioning. |

Method

1. Boroscopically inspect accessible sections of the loop.

2. Confirm absence of construction debris, weld spatter and foreign material.

3. Confirm the final flush was performed and recorded.

Acceptance criterion

No debris or foreign material. Final flush performed and recorded.

| Test instrument | Boroscope | Result | 12 sections inspected. Clean. Final flush record provided. |  |
| --- | --- | --- | --- | --- |
| Performed by |  | Pass / Fail | Pass | Date |

SAT-I-10 — Verify drain connections and air breaks.

| Test ID | SAT-I-10 |
| --- | --- |
| Traces to | URS-037 |
| Objective | Verify drain connections and air breaks. |

Method

1. Inspect every drain connection on the installed system.

2. Confirm an air break is present and visible at each.

Acceptance criterion

All drains discharge through a visible air break to prevent backflow.

| Test instrument | — | Result | All nine drains verified with visible air breaks. |  |
| --- | --- | --- | --- | --- |
| Performed by |  | Pass / Fail | Pass | Date |

SAT-I-11 — Verify pipework routing and support in classified areas.

| Test ID | SAT-I-11 |
| --- | --- |
| Traces to | URS-040 |
| Objective | Verify pipework routing and support in classified areas. |

Method

1. Inspect routing through the Grade C corridor and Grade D plant room.

2. Confirm clearance from walls and ceilings for inspection and cleaning.

3. Confirm support and finish do not compromise room cleanability.

Acceptance criterion

Routing clear of walls and ceilings, supports and finish compatible with room cleaning.

| Test instrument | Tape measure | Result | Routing clear. Two supports in the Grade C corridor have exposed threaded rod without a cleanable cover. |  |
| --- | --- | --- | --- | --- |
| Performed by |  | Pass / Fail | Fail | Date |

Comment: SDEV-007, minor.

SAT-I-12 — Verify sample point installation and identification.

| Test ID | SAT-I-12 |
| --- | --- |
| Traces to | URS-070 |
| Objective | Verify sample point installation and identification. |

Method

1. Confirm every sample point shown on the P&ID is installed.

2. Confirm each is individually tagged and matches the P&ID identifier.

3. Confirm each is accessible for sampling without contamination.

Acceptance criterion

All sample points installed, individually identified, accessible, and matching the P&ID.

| Test instrument | — | Result | All 14 sample points installed and tagged. POU-11 sample valve is 1.9 m above floor level with no platform. |  |
| --- | --- | --- | --- | --- |
| Performed by |  | Pass / Fail | Fail | Date |

Comment: SDEV-008, minor. Access platform required.

SAT-I-13 — Verify temperature mapping ports at the worst-case locations identified in the URS.

| Test ID | SAT-I-13 |
| --- | --- |
| Traces to | URS-071 |
| Objective | Verify temperature mapping ports at the worst-case locations identified in the URS. |

Method

1. Compare installed thermowells and mapping ports against the worst-case locations listed in the URS.

2. Record which locations have a port and which do not.

Acceptance criterion

A mapping port is provided at every worst-case location listed in the URS worst-case register.

| Test instrument | — | Result | No dedicated mapping ports installed. Only the four process thermowells are present. |  |
| --- | --- | --- | --- | --- |
| Performed by |  | Pass / Fail | Fail | Date |

Comment: Confirms DQ-OBS-044, unresolved through DQ, FAT and now SAT. Without ports at the least favourable points, sanitisation acceptance cannot be demonstrated at OQ. SDEV-009, critical.

SAT-I-14 — Verify the turnover documentation package.

| Test ID | SAT-I-14 |
| --- | --- |
| Traces to | URS-060 |
| Objective | Verify the turnover documentation package. |

Method

1. Review the turnover package against the URS documentation requirement.

2. Confirm weld logs, boroscopy records, slope verification records, material certificates and passivation certificate are present.

Acceptance criterion

Turnover package complete, containing every document required by URS-060.

| Test instrument | — | Result | Weld logs, material certificates and O&M manuals present. Slope verification records for site pipework absent. Boroscopy record covers skid welds only. |  |
| --- | --- | --- | --- | --- |
| Performed by |  | Pass / Fail | Fail | Date |

Comment: SDEV-010, major.

SAT-I-15 — Verify as-built drawings against the installed system.

| Test ID | SAT-I-15 |
| --- | --- |
| Traces to | Installation verification |
| Objective | Verify as-built drawings against the installed system. |

Method

1. Walk the system against the P&ID and isometrics.

2. Record every difference between the installed system and the drawings.

Acceptance criterion

As-built drawings match the installed system, with all field changes recorded.

| Test instrument | — | Result | Three field routing changes in the north bay are not reflected on ISO-011. |  |
| --- | --- | --- | --- | --- |
| Performed by |  | Pass / Fail | Fail | Date |

Comment: SDEV-011, minor. As-builts to be reissued.

# 4. Functional Test Results

SAT-F-01 — Verify the interface to the WFI generation system.

| Test ID | SAT-F-01 |
| --- | --- |
| Traces to | URS-032 |
| Objective | Verify the interface to the WFI generation system. |

Method

1. With the generation system in service, confirm the demand signal is exchanged.

2. Simulate a generation fault and confirm the status signal is received.

3. Simulate an out-of-specification diversion and confirm the signal is received and alarmed.

Acceptance criterion

Demand, status and diversion signals exchanged correctly with equipment item EQ-01.

| Test instrument | — | Result | All three signals verified. Diversion signal alarmed within 3 seconds. |  |
| --- | --- | --- | --- | --- |
| Performed by |  | Pass / Fail | Pass | Date |

SAT-F-02 — Verify the interface to the site building management system.

| Test ID | SAT-F-02 |
| --- | --- |
| Traces to | URS-033 |
| Objective | Verify the interface to the site building management system. |

Method

1. Raise three alarms and confirm annunciation at the BMS.

2. Attempt to issue a control command from the BMS.

Acceptance criterion

Alarms annunciate at the BMS. The BMS has no control authority over the WFI system.

| Test instrument | — | Result | All three alarms annunciated. No control possible from BMS. Two alarm descriptions differ between the HMI and the BMS. |  |
| --- | --- | --- | --- | --- |
| Performed by |  | Pass / Fail | Fail | Date |

Comment: SDEV-012, minor. Alarm text alignment.

SAT-F-03 — Verify time synchronisation with the site time server.

| Test ID | SAT-F-03 |
| --- | --- |
| Traces to | URS-022 |
| Objective | Verify time synchronisation with the site time server. |

Method

1. Confirm the system is synchronised to the site NTP server.

2. Attempt to alter system time at each role level.

3. Force a synchronisation and confirm the event is recorded.

Acceptance criterion

System synchronises to the site time server. Time is not user-alterable. Synchronisation events are recorded.

| Test instrument | — | Result | Synchronised to site NTP. Time alteration blocked at all roles. Sync events recorded in the audit trail. |  |
| --- | --- | --- | --- | --- |
| Performed by |  | Pass / Fail | Pass | Date |

SAT-F-04 — Verify point-of-use interfaces.

| Test ID | SAT-F-04 |
| --- | --- |
| Traces to | URS-034 |
| Objective | Verify point-of-use interfaces. |

Method

1. At each point of use, confirm the mechanical connection matches the point-of-use schedule.

2. Where a control interface is specified, confirm the signal exchange with the connected equipment.

Acceptance criterion

All point-of-use connections match the schedule. Control interfaces exchange signals as specified.

| Test instrument | — | Result | All 12 mechanical connections correct. Control interfaces to the two formulation vessels are not installed. |  |
| --- | --- | --- | --- | --- |
| Performed by |  | Pass / Fail | Fail | Date |

Comment: Confirms DQ-OBS-031. SDEV-013, major.

SAT-F-05 — Measure loop return velocity at design circulation flow.

| Test ID | SAT-F-05 |
| --- | --- |
| Traces to | URS-008 |
| Objective | Measure loop return velocity at design circulation flow. |

Method

1. Establish loop circulation at the design flow.

2. Record flow at the loop return.

3. Calculate return velocity and Reynolds number from the measured flow and the installed pipe bore.

Acceptance criterion

Return velocity not less than 1.0 m/s, or demonstrated turbulent flow with Reynolds number greater than 10,000.

| Test instrument | Calibrated flow meter, accuracy 2% of reading or better | Result | Measured 0.87 m/s at design circulation flow. Reynolds number 41,200. |  |
| --- | --- | --- | --- | --- |
| Performed by |  | Pass / Fail | Fail | Date |

Comment: Velocity below the URS figure although flow is strongly turbulent. Note that URS-008 permits either criterion; the Reynolds number criterion is met. Recorded as a fail against the velocity figure pending a user decision on which criterion applies. SDEV-014, major.

SAT-F-06 — Verify automatic duty rotation following software update.

| Test ID | SAT-F-06 |
| --- | --- |
| Traces to | URS-009 ¦ Closes FAT DEV-006 |
| Objective | Verify automatic duty rotation following software update. |

Method

1. Confirm the duty rotation function is present in the updated software.

2. Force the rotation interval and observe changeover.

3. Confirm the rotation event is recorded.

Acceptance criterion

Duty rotates automatically at a configurable interval and the event is recorded.

| Test instrument | — | Result | Rotation function present, interval configurable, changeover observed at 168 hours simulated. Event recorded. |  |
| --- | --- | --- | --- | --- |
| Performed by |  | Pass / Fail | Pass | Date |

Comment: FAT DEV-006 closed.

SAT-F-07 — Verify that the audit trail cannot be disabled, following removal of the disable function.

| Test ID | SAT-F-07 |
| --- | --- |
| Traces to | URS-030 ¦ Closes FAT DEV-009 |
| Objective | Verify that the audit trail cannot be disabled, following removal of the disable function. |

Method

1. Log in as Administrator.

2. Search the maintenance menu for any audit trail disable function.

3. Attempt to disable, edit or delete audit trail entries.

Acceptance criterion

No function exists to disable, edit or delete the audit trail, at any role level including Administrator.

| Test instrument | — | Result | Disable function removed from the software. No disable, edit or delete possible at any role. |  |
| --- | --- | --- | --- | --- |
| Performed by |  | Pass / Fail | Pass | Date |

Comment: FAT DEV-009 closed by retest against the original criterion.

SAT-F-08 — Verify audit trail export.

| Test ID | SAT-F-08 |
| --- | --- |
| Traces to | URS-031 ¦ Closes FAT DEV-010 |
| Objective | Verify audit trail export. |

Method

1. Filter the audit trail by date range and user.

2. Export the filtered record.

3. Confirm the export is human-readable and retains metadata.

Acceptance criterion

Audit trail exportable over a selected period, human-readable, retaining metadata.

| Test instrument | — | Result | Export produced in CSV and PDF. Metadata retained. |  |
| --- | --- | --- | --- | --- |
| Performed by |  | Pass / Fail | Pass | Date |

Comment: FAT DEV-010 closed.

SAT-F-09 — Verify the sanitisation start interlock following modification.

| Test ID | SAT-F-09 |
| --- | --- |
| Traces to | URS-055 ¦ Closes FAT DEV-007 |
| Objective | Verify the sanitisation start interlock following modification. |

Method

1. Open a point of use to an operator-accessible outlet.

2. Attempt to initiate a sanitisation cycle.

3. Close the point of use and repeat.

Acceptance criterion

Sanitisation cannot be initiated while any point of use is open to an operator-accessible outlet.

| Test instrument | — | Result | Sanitisation start correctly blocked with POU-03 open. Started normally with all points closed. |  |
| --- | --- | --- | --- | --- |
| Performed by |  | Pass / Fail | Pass | Date |

Comment: FAT DEV-007 closed.

SAT-F-10 — Verify sanitisation start confirmation and point-of-use lockout indication.

| Test ID | SAT-F-10 |
| --- | --- |
| Traces to | URS-056 |
| Objective | Verify sanitisation start confirmation and point-of-use lockout indication. |

Method

1. Initiate a sanitisation cycle.

2. Confirm a positive confirmation step is required.

3. Confirm point-of-use lockout indication is visible at each point.

Acceptance criterion

Positive confirmation required before start. Every point of use visibly indicated as locked out for the duration.

| Test instrument | — | Result | Confirmation step present. Lockout indication present at 10 of 12 points; POU-09 and POU-11 have no local indicator. |  |
| --- | --- | --- | --- | --- |
| Performed by |  | Pass / Fail | Fail | Date |

Comment: SDEV-015, major.

SAT-F-11 — Verify sanitisation cycle completion logic following modification.

| Test ID | SAT-F-11 |
| --- | --- |
| Traces to | URS-049 ¦ Closes FAT DEV-011 |
| Objective | Verify sanitisation cycle completion logic following modification. |

Method

1. Initiate a cycle in simulation mode.

2. Force a simulated low temperature at one monitored location.

3. Observe the cycle outcome.

Acceptance criterion

The cycle cannot be declared successful where any monitored location failed to achieve the required temperature and hold.

| Test instrument | — | Result | With a forced low temperature the cycle now reports Failed and raises an alarm. However the acceptance temperature and hold time remain [TO BE CONFIRMED] in URS-014, so the values used are supplier defaults. |  |
| --- | --- | --- | --- | --- |
| Performed by |  | Pass / Fail | Fail | Date |

Comment: The logic defect is corrected, but the acceptance values are still undefined in the specification, so the cycle cannot be qualified. FAT DEV-011 partially closed. See Section 11.

SAT-F-12 — Verify the initiating operator is recorded on the sanitisation record.

| Test ID | SAT-F-12 |
| --- | --- |
| Traces to | URS-018 ¦ Closes FAT DEV-013 |
| Objective | Verify the initiating operator is recorded on the sanitisation record. |

Method

1. Run a simulated cycle under a named account.

2. Review the cycle record.

Acceptance criterion

The cycle record contains the temperature profile, hold achieved, initiating operator and outcome.

| Test instrument | — | Result | All four elements recorded including the initiating operator. |  |
| --- | --- | --- | --- | --- |
| Performed by |  | Pass / Fail | Pass | Date |

Comment: FAT DEV-013 closed.

SAT-F-13 — Verify calibration parameter access restriction following the user decision.

| Test ID | SAT-F-13 |
| --- | --- |
| Traces to | URS-027 ¦ Closes FAT DEV-008 |
| Objective | Verify calibration parameter access restriction following the user decision. |

Method

1. Confirm the user decision on whether Supervisor is an authorised role.

2. Attempt to change calibration parameters at each role level.

Acceptance criterion

Critical setpoints and calibration parameters modifiable only by roles the user has authorised, with every change recorded.

| Test instrument | — | Result | User confirmed Supervisor is an authorised role for calibration parameters, recorded in the change control. Access verified as configured; all changes recorded. |  |
| --- | --- | --- | --- | --- |
| Performed by |  | Pass / Fail | Pass | Date |

Comment: FAT DEV-008 closed by documented user decision, not by rework.

SAT-F-14 — Verify elastomer compliance documentation.

| Test ID | SAT-F-14 |
| --- | --- |
| Traces to | URS-045 ¦ Closes FAT DEV-014 |
| Objective | Verify elastomer compliance documentation. |

Method

1. Review the revised elastomer schedule.

2. Confirm compliance statements and stated service life at loop temperature.

Acceptance criterion

Elastomers comply with USP Class VI and 21 CFR 177.2600, with stated service life at continuous loop temperature.

| Test instrument | — | Result | Revised schedule provides both compliance statements and a stated service life of 24 months at 85 degrees C continuous. |  |
| --- | --- | --- | --- | --- |
| Performed by |  | Pass / Fail | Pass | Date |

Comment: FAT DEV-014 closed.

SAT-F-15 — Verify in-place vent filter integrity testing following modification.

| Test ID | SAT-F-15 |
| --- | --- |
| Traces to | URS-012 ¦ Closes FAT DEV-005 |
| Objective | Verify in-place vent filter integrity testing following modification. |

Method

1. Confirm the integrity test connection is installed.

2. Perform an integrity test with the filter in place.

3. Confirm the sterile boundary is not broken during the test.

Acceptance criterion

Integrity testing possible in place, without breaking the sterile boundary.

| Test instrument | Filter integrity tester | Result | Test connection installed. Integrity test performed in place. Sterile boundary maintained. |  |
| --- | --- | --- | --- | --- |
| Performed by |  | Pass / Fail | Pass | Date |

Comment: FAT DEV-005 closed.

SAT-F-16 — Repeat spray ball coverage test following modification.

| Test ID | SAT-F-16 |
| --- | --- |
| Traces to | URS-011 ¦ Closes FAT DEV-004 |
| Objective | Repeat spray ball coverage test following modification. |

Method

1. Coat the vessel internal surface including headspace with riboflavin.

2. Operate the spray ball at design flow and pressure.

3. Inspect all internal surfaces under ultraviolet light.

Acceptance criterion

No residual fluorescence on any internal surface including the headspace and internal fittings.

| Test instrument | UV inspection lamp, riboflavin solution | Result | No residual fluorescence. Coverage complete including the level probe boss and vent nozzle. |  |
| --- | --- | --- | --- | --- |
| Performed by |  | Pass / Fail | Pass | Date |

Comment: FAT DEV-004 closed by retest against the original criterion.

SAT-F-17 — Verify drainability of the reworked skid branches.

| Test ID | SAT-F-17 |
| --- | --- |
| Traces to | URS-046 ¦ Closes FAT DEV-002 |
| Objective | Verify drainability of the reworked skid branches. |

Method

1. Fill the skid pipework.

2. Drain and inspect the two reworked branches.

Acceptance criterion

No retained water in the reworked branches.

| Test instrument | — | Result | Both reworked branches now drain fully. |  |
| --- | --- | --- | --- | --- |
| Performed by |  | Pass / Fail | Pass | Date |

Comment: FAT DEV-002 closed.

SAT-F-18 — Verify slope of the re-supported skid runs.

| Test ID | SAT-F-18 |
| --- | --- |
| Traces to | URS-039 ¦ Closes FAT DEV-003 |
| Objective | Verify slope of the re-supported skid runs. |

Method

1. Measure fall on the two runs re-supported after FAT.

Acceptance criterion

Fall not less than 1 in 100.

| Test instrument | Digital level | Result | Both runs now at 1:92 and 1:88. |  |
| --- | --- | --- | --- | --- |
| Performed by |  | Pass / Fail | Pass | Date |

Comment: FAT DEV-003 closed. Note this does not close SAT-I-05, which concerns site pipework.

SAT-F-19 — Verify the disposition agreed for the loop return conductivity cell.

| Test ID | SAT-F-19 |
| --- | --- |
| Traces to | URS-051 ¦ Closes FAT DEV-012 |
| Objective | Verify the disposition agreed for the loop return conductivity cell. |

Method

1. Confirm the concession recorded in change control.

2. Confirm the isolation arrangement, if provided.

Acceptance criterion

Instrument removable without breaching the loop, or a documented concession accepted by Quality Assurance.

| Test instrument | — | Result | Concession accepted; calibration to be performed during planned shutdown, recorded in the maintenance schedule. |  |
| --- | --- | --- | --- | --- |
| Performed by |  | Pass / Fail | Pass | Date |

Comment: FAT DEV-012 closed by concession.

SAT-F-20 — Verify training delivery.

| Test ID | SAT-F-20 |
| --- | --- |
| Traces to | URS-062 |
| Objective | Verify training delivery. |

Method

1. Confirm training was delivered to operators, maintenance, QA and validation personnel.

2. Review attendance records and training content.

Acceptance criterion

Training delivered to all groups required by URS-062, covering operation, maintenance, audit trail review and user administration.

| Test instrument | — | Result | Operator and maintenance training delivered. QA and validation training on audit trail review and user administration not yet delivered. |  |
| --- | --- | --- | --- | --- |
| Performed by |  | Pass / Fail | Fail | Date |

Comment: SDEV-016, major.

SAT-F-21 — Verify point-of-use cooler arrangement.

| Test ID | SAT-F-21 |
| --- | --- |
| Traces to | URS-013 |
| Objective | Verify point-of-use cooler arrangement. |

Method

1. Inspect the installed system for point-of-use coolers at the four points requiring water below loop temperature.

Acceptance criterion

Point-of-use coolers installed at every point of use requiring water below loop temperature.

| Test instrument | — | Result | No coolers installed. The design does not include them. |  |
| --- | --- | --- | --- | --- |
| Performed by |  | Pass / Fail | Fail | Date |

Comment: Unresolved from DQ-OBS-011 through FAT and SAT. Four points of use cannot be served as specified. SDEV-017, critical. Design resolution required before OQ.

SAT-F-22 — Verify data export for laboratory correlation.

| Test ID | SAT-F-22 |
| --- | --- |
| Traces to | URS-035 |
| Objective | Verify data export for laboratory correlation. |

Method

1. Attempt to export online monitoring data in a defined format.

Acceptance criterion

Online monitoring data exportable in a defined format for correlation with laboratory results.

| Test instrument | — | Result | No export capability. Not in the design. |  |
| --- | --- | --- | --- | --- |
| Performed by |  | Pass / Fail | Fail | Date |

Comment: Confirms DQ-OBS-033. Desirable requirement. SDEV-018, minor.

SAT-F-23 — Confirm 21 CFR Part 11 applicability and scope.

| Test ID | SAT-F-23 |
| --- | --- |
| Traces to | URS-066 |
| Objective | Confirm 21 CFR Part 11 applicability and scope. |

Method

1. Confirm with the site whether Part 11 applies.

2. Where it applies, confirm the supplier scope includes the required controls.

Acceptance criterion

Part 11 applicability confirmed and, where applicable, the required controls are within the scope of supply.

| Test instrument | — | Result | Site confirmed Part 11 applies. Supplier scope includes access control, audit trail and record retention. Electronic signature is not in scope and is not required by URS-025 to URS-031. |  |
| --- | --- | --- | --- | --- |
| Performed by |  | Pass / Fail | Pass | Date |

Comment: Closes DQ-OBS-047.

SAT-F-24 — Verify instrument loop checks on the installed system.

| Test ID | SAT-F-24 |
| --- | --- |
| Traces to | URS-017 |
| Objective | Verify instrument loop checks on the installed system. |

Method

1. For each installed instrument, apply a simulated input at 0, 50 and 100 percent of span.

2. Confirm the value at the HMI and the recorded value.

3. Confirm calibration certificates are current.

Acceptance criterion

Every loop reads correctly at three points within instrument accuracy, with current calibration certificates.

| Test instrument | Calibrated signal simulator | Result | All 17 installed loops verified. All calibration certificates current. |  |
| --- | --- | --- | --- | --- |
| Performed by |  | Pass / Fail | Pass | Date |

# 5. Factory Acceptance Deviation Closure

| FAT dev | Class | Verified by | Outcome | Status |
| --- | --- | --- | --- | --- |
| DEV-001 | Critical | SAT-I-07 | Eight of nine reworked branches now at or below 3D; one at 3.4D. Two site-installed branches also exceed 3D. | Not closed |
| DEV-002 | Major | SAT-F-17 | Both reworked skid branches now drain fully. | Closed |
| DEV-003 | Major | SAT-F-18 | Both re-supported runs now at 1:92 and 1:88. | Closed |
| DEV-004 | Major | SAT-F-16 | Coverage test repeated; no residual fluorescence. | Closed |
| DEV-005 | Major | SAT-F-15 | Integrity test connection installed; test performed in place. | Closed |
| DEV-006 | Major | SAT-F-06 | Duty rotation function added and verified. | Closed |
| DEV-007 | Critical | SAT-F-09 | Sanitisation start interlock added and verified. | Closed |
| DEV-008 | Minor | SAT-F-13 | User confirmed Supervisor as an authorised role, recorded in change control. | Closed by concession |
| DEV-009 | Critical | SAT-F-07 | Disable function removed from the software; retested at all role levels. | Closed |
| DEV-010 | Major | SAT-F-08 | Audit trail export function provided and verified. | Closed |
| DEV-011 | Critical | SAT-F-11 | Completion logic corrected, but acceptance values remain undefined in URS-014. | Not closed |
| DEV-012 | Minor | SAT-F-19 | Concession accepted; calibration during planned shutdown. | Closed by concession |
| DEV-013 | Major | SAT-F-12 | Initiating operator now recorded on the cycle record. | Closed |
| DEV-014 | Minor | SAT-F-14 | Compliance statements and service life provided. | Closed |

# 6. Requirements Deferred from Factory Acceptance — Disposition

| URS ID | Disposition | Test / stage | Basis |
| --- | --- | --- | --- |
| URS-001 | Deferred again | PQ | WFI quality against the monograph requires the system in service with laboratory testing. |
| URS-002 | Deferred again | OQ | Peak demand remains [TO BE CONFIRMED] in the URS. No criterion exists to test against. |
| URS-003 | Deferred again | PQ | Requires extended operation in service. |
| URS-004 | Deferred again | OQ | Tank capacity requirement remains [TO BE CONFIRMED] in the URS. Installed vessel is 5,000 L. |
| URS-005 | Verified at SAT | SAT-F-04 | 12 points of use installed and verified against the schedule. |
| URS-006 | Deferred again | PQ | Requires operation in service following a planned shutdown. |
| URS-007 | Deferred again | OQ | Requires loop at operating temperature with mapping at the least favourable point. Mapping ports are not installed; see SAT-I-13. |
| URS-008 | Verified at SAT | SAT-F-05 | Return velocity measured at design circulation flow. Result 0.87 m/s; see SDEV-014. |
| URS-013 | Verified at SAT | SAT-F-21 | Verified as not installed. Design resolution required. |
| URS-014 | Deferred again | OQ | Sanitisation temperature and hold time remain [TO BE CONFIRMED] in the URS. |
| URS-016 | Deferred again | OQ | Minimum pressure at the remote point remains [TO BE CONFIRMED] in the URS. |
| URS-020 | Deferred again | OQ | Retention period remains [TO BE CONFIRMED] in the URS. |
| URS-021 | Deferred again | OQ | Enduring and available over the retention period requires operation in service. |
| URS-022 | Verified at SAT | SAT-F-03 | Synchronised to the site time server. |
| URS-032 | Verified at SAT | SAT-F-01 | Interface to EQ-01 verified. |
| URS-033 | Verified at SAT | SAT-F-02 | BMS interface verified; alarm text mismatch raised. |
| URS-034 | Verified at SAT | SAT-F-04 | Mechanical interfaces verified; control interfaces not installed. |
| URS-035 | Verified at SAT | SAT-F-22 | Verified as not provided. |
| URS-036 | Not executed | SAT-I-04 | Utility envelope remains [TO BE CONFIRMED] in the URS. Values recorded for information. |
| URS-037 | Verified at SAT | SAT-I-10 | All drains verified with air breaks. |
| URS-039 | Verified at SAT | SAT-I-05 | Site pipework slope measured; two runs below requirement. |
| URS-040 | Verified at SAT | SAT-I-11 | Routing verified; support finish finding raised. |
| URS-043 | Verified at SAT | SAT-I-08 | Passivation certificate covers skid only. |
| URS-063 | Deferred again | PQ | Water quality against the monograph requires the system in service. |
| URS-064 | Deferred again | PQ | Requires WFI in service and laboratory testing. |
| URS-069 | Deferred again | PQ | The three-phase programme runs in service over one year. |
| URS-070 | Verified at SAT | SAT-I-12 | Sample points installed and identified; access finding raised. |
| URS-071 | Verified at SAT | SAT-I-13 | Verified as not installed. Blocks OQ sanitisation qualification. |
| URS-072 | Outstanding | DQ closure | Hydraulic calculation at the worst-case demand condition remains outstanding at DQ-OBS-045. |
| URS-073 | Deferred again | VSR | Traceability across the programme is closed at the Validation Summary Report. |
| URS-074 | Deferred again | OQ | Ability to challenge worst-case conditions is confirmed in operation. |
| URS-059 | Verified at SAT | — | SAT protocol was provided for review before testing. |
| URS-060 | Verified at SAT | SAT-I-14 | Turnover package incomplete; see SDEV-010. |
| URS-062 | Verified at SAT | SAT-F-20 | Training partially delivered; see SDEV-016. |
| URS-065 | Deferred again | VSR | Assessed across the qualification programme. |
| URS-066 | Verified at SAT | SAT-F-23 | Part 11 applicability confirmed. |

# 7. Worst-Case Condition Outcomes

| Ref | Condition | At SAT | Basis | Outcome / deferral |
| --- | --- | --- | --- | --- |
| WC-07 | Longest branch and standby pump leg | Challenged | SAT-I-07 measured every branch on the installed system. SAT-F-06 verified duty rotation. | Duty rotation now closed. Three branches still exceed 3D; SDEV-001. |
| WC-09 | Highest point and longest horizontal run | Challenged | SAT-I-05 and SAT-I-06 measured slope and drainability across the complete installed system. | Two runs below slope requirement and one branch retains water. SDEV-002 and SDEV-003. |
| WC-05 | Tank at minimum operating level | Re-challenged | SAT-F-16 repeated the spray ball coverage test after modification. | Closed. Coverage complete including headspace. |
| WC-06 | Maximum tank discharge rate | Closed at FAT | Verified at FAT-011 and confirmed unchanged by installation. | No further action. |
| WC-01 | Maximum simultaneous demand | Not challengeable at SAT | Requires all points of use in service drawing simultaneously, which is an operational condition. | Deferred to OQ. Supplier hydraulic calculation at this condition still outstanding at DQ-OBS-045. |
| WC-02 | Coldest point during normal circulation | Not challengeable at SAT | Requires mapping at the least favourable point. Mapping ports are not installed. | Deferred to OQ and blocked by SDEV-009. |
| WC-03 | Least favourable point during sanitisation | Not challengeable at SAT | Requires mapping ports and defined acceptance values. | Deferred to OQ and blocked by SDEV-009 and by the undefined values in URS-014. |
| WC-04 | Point-of-use cooler branch | Not challengeable | No coolers installed. | Blocked by SDEV-017. Cannot be challenged at any stage until the design is resolved. |
| WC-08 | Most hydraulically remote point of use | Not challengeable at SAT | Requires operational draw at the remote point. | Deferred to OQ. |
| WC-10 | Extended low-demand period | Not challengeable at SAT | Requires extended operation in service. | Deferred to PQ. |
| WC-11 | Worst-case feed water quality | Not challengeable at SAT | Requires seasonal variation in service. | Deferred to PQ Phase 3. |

# 8. Deviation Register

| Ref | Class | Test | Description | Disposition / status |
| --- | --- | --- | --- | --- |
| SDEV-001 | Critical | SAT-I-07 | Three branches exceed the 3D dead leg limit: one reworked skid branch at 3.4D and two site-installed branches at 3.6D and 4.1D. | Contractor to rework the two site branches. Supplier to address the remaining skid branch. Retest before OQ. Status: Open |
| SDEV-002 | Major | SAT-I-05 | Two site-installed runs in the north bay have a fall of 1:130 against the 1:100 required by URS-039. | Contractor to re-support both runs. Retest before OQ. Status: Open |
| SDEV-003 | Critical | SAT-I-06 | The branch serving POU-07 retains water after draining. | Contractor to modify the branch geometry. Retest before OQ. Status: Open |
| SDEV-004 | Minor | SAT-I-02 | Clearance to the east wall is 640 mm against 750 mm drawn, restricting access to the heat exchanger head. | User to accept by concession or relocate. Maintenance access assessment required. Status: Open |
| SDEV-005 | Minor | SAT-I-03 | Two pipe supports missing on the north riser. | Contractor to fit. Punch item. Status: Open |
| SDEV-006 | Major | SAT-I-08 | Passivation certificate covers the skid only; site-installed pipework was not passivated. | Contractor to passivate site-installed pipework and issue a certificate covering the complete system. Retest before OQ. Status: Open |
| SDEV-007 | Minor | SAT-I-11 | Two supports in the Grade C corridor have exposed threaded rod without a cleanable cover. | Contractor to fit covers. Status: Open |
| SDEV-008 | Minor | SAT-I-12 | Sample valve at POU-11 is 1.9 m above floor level with no access platform. | User to provide a fixed platform or accept sampling from a step. EHS assessment required. Status: Open |
| SDEV-009 | Critical | SAT-I-13 | No temperature mapping ports installed at the worst-case locations listed in the URS worst-case register. | Contractor to install mapping ports at the locations identified in the URS. Without them, sanitisation acceptance cannot be demonstrated at OQ. Unresolved since DQ-OBS-044. Status: Open |
| SDEV-010 | Major | SAT-I-14 | Turnover package incomplete: slope verification records for site pipework absent, boroscopy record covers skid welds only. | Contractor to complete the turnover package before IQ. Status: Open |
| SDEV-011 | Minor | SAT-I-15 | Three field routing changes in the north bay are not reflected on ISO-011. | Contractor to reissue as-built isometrics. Status: Open |
| SDEV-012 | Minor | SAT-F-02 | Two alarm descriptions differ between the HMI and the BMS. | Supplier to align alarm text. Status: Open |
| SDEV-013 | Major | SAT-F-04 | Control interfaces to the two formulation vessels are not installed. | Confirm scope. Unresolved since DQ-OBS-031. Status: Open |
| SDEV-014 | Major | SAT-F-05 | Measured return velocity 0.87 m/s against the 1.0 m/s stated in URS-008, although Reynolds number 41,200 satisfies the alternative turbulent flow criterion in the same requirement. | User decision required on which criterion applies. If the velocity figure is retained, the loop requires hydraulic modification. Note that URS-008 records 1 m/s as a design convention, not a regulatory limit. Status: Open |
| SDEV-015 | Major | SAT-F-10 | Point-of-use lockout indication absent at POU-09 and POU-11. | Supplier to fit local indicators. Status: Open |
| SDEV-016 | Major | SAT-F-20 | Training for QA and validation personnel on audit trail review and user administration not delivered. | Supplier to deliver before OQ. Status: Open |
| SDEV-017 | Critical | SAT-F-21 | No point-of-use coolers installed. Four points of use require water below loop temperature and cannot be served as specified. | Design resolution required. Unresolved since DQ-OBS-011. This is a scope gap, not an installation defect. Status: Open |
| SDEV-018 | Minor | SAT-F-22 | No data export capability for laboratory correlation. | Desirable requirement. Confirm whether it is carried forward. Status: Open |

# 9. Punch List

| Item | Description | Against | Owner | Due |
| --- | --- | --- | --- | --- |
| SPL-01 | Rework three branches exceeding 3D | SDEV-001 | Contractor / Supplier | Before OQ |
| SPL-02 | Re-support two north bay runs to 1:100 | SDEV-002 | Contractor | Before OQ |
| SPL-03 | Modify POU-07 branch to drain | SDEV-003 | Contractor | Before OQ |
| SPL-04 | Passivate site-installed pipework and issue certificate | SDEV-006 | Contractor | Before OQ |
| SPL-05 | Install temperature mapping ports at URS worst-case locations | SDEV-009 | Contractor | Before OQ |
| SPL-06 | Fit two missing pipe supports on north riser | SDEV-005 | Contractor | Before IQ |
| SPL-07 | Complete turnover package | SDEV-010 | Contractor | Before IQ |
| SPL-08 | Reissue as-built isometrics | SDEV-011 | Contractor | Before IQ |
| SPL-09 | Fit cleanable covers to Grade C supports | SDEV-007 | Contractor | Before IQ |
| SPL-10 | Align HMI and BMS alarm text | SDEV-012 | Supplier | Before OQ |
| SPL-11 | Fit lockout indicators at POU-09 and POU-11 | SDEV-015 | Supplier | Before OQ |
| SPL-12 | Deliver QA and validation training | SDEV-016 | Supplier | Before OQ |
| SPL-13 | Resolve point-of-use cooler scope | SDEV-017 | User / Supplier | Before OQ |
| SPL-14 | Decide velocity criterion for URS-008 | SDEV-014 | User | Before OQ |
| SPL-15 | Fix sanitisation temperature and hold time in URS-014 | DEV-011 | User | Before OQ |
| SPL-16 | Fix boroscopy percentage in URS-042 | FAT PL-013 | User | Before IQ |
| SPL-17 | Provide access platform or accept concession at POU-11 | SDEV-008 | User | Before OQ |
| SPL-18 | Confirm control interface scope for formulation vessels | SDEV-013 | User | Before OQ |

# 10. Requirements Remaining to be Verified

The following are not verified at Site Acceptance and are carried into Installation, Operational and Performance Qualification. This list is the direct input to the Installation Qualification protocol.

| URS ID | Verified at | Reason not verified at Site Acceptance |
| --- | --- | --- |
| URS-001 | PQ | WFI quality against the monograph requires the system in service with laboratory testing. |
| URS-002 | OQ | Peak demand remains [TO BE CONFIRMED] in the URS. No criterion exists to test against. |
| URS-003 | PQ | Requires extended operation in service. |
| URS-004 | OQ | Tank capacity requirement remains [TO BE CONFIRMED] in the URS. Installed vessel is 5,000 L. |
| URS-006 | PQ | Requires operation in service following a planned shutdown. |
| URS-007 | OQ | Requires loop at operating temperature with mapping at the least favourable point. Mapping ports are not installed; see SAT-I-13. |
| URS-014 | OQ | Sanitisation temperature and hold time remain [TO BE CONFIRMED] in the URS. |
| URS-016 | OQ | Minimum pressure at the remote point remains [TO BE CONFIRMED] in the URS. |
| URS-020 | OQ | Retention period remains [TO BE CONFIRMED] in the URS. |
| URS-021 | OQ | Enduring and available over the retention period requires operation in service. |
| URS-036 | SAT-I-04 | Utility envelope remains [TO BE CONFIRMED] in the URS. Values recorded for information. |
| URS-063 | PQ | Water quality against the monograph requires the system in service. |
| URS-064 | PQ | Requires WFI in service and laboratory testing. |
| URS-069 | PQ | The three-phase programme runs in service over one year. |
| URS-072 | DQ closure | Hydraulic calculation at the worst-case demand condition remains outstanding at DQ-OBS-045. |
| URS-073 | VSR | Traceability across the programme is closed at the Validation Summary Report. |
| URS-074 | OQ | Ability to challenge worst-case conditions is confirmed in operation. |
| URS-065 | VSR | Assessed across the qualification programme. |

# 11. Conclusion

Of 39 tests defined in SAT-WFI-001 Revision 0.1: 19 passed, 19 failed and 1 could not be executed because the acceptance criterion is not defined in URS-WFI-001.

18 deviations were raised at Site Acceptance: 4 critical, 7 major and 7 minor. 12 of 14 Factory Acceptance deviations were closed; 2 remain open. 18 punch list items are recorded.

Of the eleven worst-case conditions identified in URS-WFI-001, two were challenged at site, one was re-challenged and closed, one had been closed at Factory Acceptance, and seven remain deferred to Operational or Performance Qualification. One of those seven cannot be challenged at any stage until the point-of-use cooler scope is resolved.

The system is [ accepted for qualification / accepted subject to closure of the punch list / not accepted ].

The bracketed judgement is drafted from the results recorded in this document. It is a judgement for the reviewer and must be confirmed, amended or replaced by qualified personnel before this report is issued. Pharma4i does not make this determination.

Note for the reviewer: four critical deviations are open. Three concern the installed pipework and are correctable. The fourth, SDEV-017, is a scope gap rather than a defect — no point-of-use coolers exist and four points of use cannot be served as specified. That has been visible since DQ-OBS-011 and has now passed through three qualification stages unresolved. Separately, SDEV-009 blocks Operational Qualification entirely: without mapping ports at the worst-case locations, sanitisation acceptance cannot be demonstrated at the least favourable point. On the results recorded here, a conclusion of accepted for qualification would not be supportable.

# 12. Attendance and Signatures

The persons below witnessed execution and confirm that the results recorded in this report are those observed at site.

| Role | Name | Department | Signature | Date |
| --- | --- | --- | --- | --- |
| Author |  | Engineering |  |  |
| Reviewer |  | CQV / Validation |  |  |
| Reviewer |  | Operations |  |  |
| Reviewer |  | Automation / IT |  |  |
| Reviewer |  | EHS |  |  |
| Reviewer |  | Contamination Control |  |  |
| Quality approval |  | Quality Assurance |  |  |

# 13. Revision History

| Revision | Date | Description of change | Author |
| --- | --- | --- | --- |
| 0.1 | [DD-MMM-YYYY] | First draft. |  |

# Appendix A — Traceability across URS, DQ, FAT and SAT

| URS ID | Requirement summary | DQ verdict | FAT | SAT test | SAT result |
| --- | --- | --- | --- | --- | --- |
| URS-001 | The system shall store and distribute Water for Injection meeting the requirements of… | see DQ-WFI-001 | Deferred | — | Deferred again |
| URS-002 | The system shall deliver a peak instantaneous demand of [TO BE CONFIRMED] L/min and a… | see DQ-WFI-001 | Deferred | — | Deferred again |
| URS-003 | The system shall operate continuously, 24 hours per day, 7 days per week, with planne… | see DQ-WFI-001 | Deferred | — | Deferred again |
| URS-004 | The storage tank shall have a nominal capacity of [TO BE CONFIRMED] L, sized to buffe… | see DQ-WFI-001 | Deferred | — | Deferred again |
| URS-005 | The distribution loop shall serve [TO BE CONFIRMED] points of use, listed with their … | see DQ-WFI-001 | Deferred | — | Verified at SAT |
| URS-006 | The system shall recover to full specification within [TO BE CONFIRMED] hours followi… | see DQ-WFI-001 | Deferred | — | Deferred again |
| URS-007 | WFI shall be stored and distributed under continuous hot circulation at a temperature… | see DQ-WFI-001 | Deferred | — | Deferred again |
| URS-008 | The distribution loop shall maintain a return flow velocity of not less than 1.0 m/s,… | see DQ-WFI-001 | Deferred | SAT-F-05 | Fail |
| URS-009 | The system shall be fitted with duty and standby distribution pumps with automatic ch… | see DQ-WFI-001 | Tested | SAT-F-06 | Pass |
| URS-010 | Loop temperature shall be maintained by a heat exchanger of double tube sheet constru… | see DQ-WFI-001 | Tested | — | — |
| URS-011 | The storage tank shall be fitted with a spray ball providing demonstrated full wetted… | see DQ-WFI-001 | Tested | SAT-F-16 | Pass |
| URS-012 | The storage tank shall be fitted with a hydrophobic vent filter of 0.22 micrometre ra… | see DQ-WFI-001 | Tested | SAT-F-15 | Pass |
| URS-013 | Points of use requiring water below loop temperature shall be served by dedicated poi… | see DQ-WFI-001 | Deferred | SAT-F-21 | Fail |
| URS-014 | The system shall provide a thermal sanitisation cycle capable of raising every point … | see DQ-WFI-001 | Deferred | — | Deferred again |
| URS-015 | Tank level shall be controlled automatically, with high, high-high, low and low-low a… | see DQ-WFI-001 | Tested | — | — |
| URS-016 | The system shall deliver a minimum dynamic pressure of [TO BE CONFIRMED] bar g at the… | see DQ-WFI-001 | Deferred | — | Deferred again |
| URS-017 | The control system shall continuously record loop supply temperature, loop return tem… | see DQ-WFI-001 | Tested | SAT-F-24 | Pass |
| URS-018 | The system shall record every sanitisation cycle, capturing the temperature profile a… | see DQ-WFI-001 | Tested | SAT-F-12 | Pass |
| URS-019 | All alarms shall be recorded with the alarm condition, time of onset, time of acknowl… | see DQ-WFI-001 | Tested | — | — |
| URS-020 | Records shall be retained for not less than [TO BE CONFIRMED] years and shall be expo… | see DQ-WFI-001 | Deferred | — | Deferred again |
| URS-021 | Records shall be attributable, legible, contemporaneous, original and accurate, and s… | see DQ-WFI-001 | Deferred | — | Deferred again |
| URS-022 | The system clock shall synchronise with the site time server. Users shall not be able… | see DQ-WFI-001 | Deferred | SAT-F-03 | Pass |
| URS-023 | The system shall support automated backup of all GMP records, and restoration of thos… | see DQ-WFI-001 | Tested | — | — |
| URS-024 | No function shall permit deletion or overwriting of a recorded value. Corrections sha… | see DQ-WFI-001 | Tested | — | — |
| URS-025 | The control system shall provide role-based access control with individual named user… | see DQ-WFI-001 | Tested | — | — |
| URS-026 | The system shall provide at least the roles Operator, Supervisor, Engineer and Admini… | see DQ-WFI-001 | Tested | — | — |
| URS-027 | Critical setpoints, including sanitisation temperature and hold time, alarm limits an… | see DQ-WFI-001 | Tested | SAT-F-13 | Pass |
| URS-028 | The system shall enforce automatic session timeout after a configurable period of ina… | see DQ-WFI-001 | Tested | — | — |
| URS-029 | The system shall maintain a secure, computer-generated, time-stamped audit trail reco… | see DQ-WFI-001 | Tested | — | — |
| URS-030 | The audit trail shall not be editable or disableable by any user, including administr… | see DQ-WFI-001 | Tested | SAT-F-07 | Pass |
| URS-031 | The system shall support periodic audit trail review, with a filterable view and an e… | see DQ-WFI-001 | Tested | SAT-F-08 | Pass |
| URS-032 | The system shall interface with the upstream WFI generation system, exchanging demand… | see DQ-WFI-001 | Deferred | SAT-F-01 | Pass |
| URS-033 | The system shall provide monitored signals to the site building management system for… | see DQ-WFI-001 | Deferred | SAT-F-02 | Fail |
| URS-034 | The system shall provide the physical and electrical interface at each point of use d… | see DQ-WFI-001 | Deferred | SAT-F-04 | Fail |
| URS-035 | Where sample results are managed in a laboratory information management system, the s… | see DQ-WFI-001 | Deferred | SAT-F-22 | Fail |
| URS-036 | The system shall operate within the site utility envelope: electrical supply [TO BE C… | see DQ-WFI-001 | Deferred | SAT-I-04 | Not executed |
| URS-037 | All drain connections shall discharge through an air break to prevent backflow, and s… | see DQ-WFI-001 | Deferred | SAT-I-10 | Pass |
| URS-038 | All hot surfaces accessible to personnel shall be insulated or guarded such that touc… | see DQ-WFI-001 | Tested | — | — |
| URS-039 | Pipework shall be installed with a continuous fall of not less than 1 in 100 towards … | see DQ-WFI-001 | Deferred | SAT-I-05 | Fail |
| URS-040 | Loop pipework routed through classified areas shall be finished and supported so as n… | see DQ-WFI-001 | Deferred | SAT-I-11 | Fail |
| URS-041 | All product contact surfaces shall be stainless steel 316L, with a mechanically polis… | see DQ-WFI-001 | Tested | — | — |
| URS-042 | All product contact welds shall be automatic orbital welds. A weld log shall be maint… | see DQ-WFI-001 | Tested | — | — |
| URS-043 | The system shall be passivated after installation in accordance with a documented pro… | see DQ-WFI-001 | Deferred | SAT-I-08 | Fail |
| URS-044 | Material certificates in accordance with EN 10204 Type 3.1 shall be provided for all … | see DQ-WFI-001 | Tested | — | — |
| URS-045 | Elastomers and polymers in product contact shall comply with USP Class VI and 21 CFR … | see DQ-WFI-001 | Tested | SAT-F-14 | Pass |
| URS-046 | All valves in product contact shall be sanitary diaphragm valves of zero static or ze… | see DQ-WFI-001 | Tested | SAT-F-17 | Pass |
| URS-047 | No dead leg in the distribution system shall exceed three internal pipe diameters (3D… | see DQ-WFI-001 | Tested | SAT-I-07 | Fail |
| URS-048 | The complete system, including the tank, loop, all branches and all points of use, sh… | see DQ-WFI-001 | Tested | SAT-I-06 | Fail |
| URS-049 | The sanitisation cycle shall be initiated from the operator interface, shall run auto… | see DQ-WFI-001 | Tested | SAT-F-11 | Fail |
| URS-050 | Sample valves at each sampling location shall be of sanitary design, self-draining, a… | see DQ-WFI-001 | Tested | — | — |
| URS-051 | All instruments requiring calibration shall be accessible without dismantling major a… | see DQ-WFI-001 | Tested | SAT-F-19 | Pass |
| URS-052 | The supplier shall provide a preventive maintenance schedule stating each task, its f… | see DQ-WFI-001 | Tested | — | — |
| URS-053 | The storage tank shall be protected against overpressure and vacuum by a rupture disc… | see DQ-WFI-001 | Tested | — | — |
| URS-054 | An emergency stop shall be provided at the skid and at each remote pump location, pla… | see DQ-WFI-001 | Tested | — | — |
| URS-055 | Interlocks shall prevent operation of distribution pumps against a closed system and … | see DQ-WFI-001 | Tested | SAT-F-09 | Pass |
| URS-056 | Sanitisation shall not be capable of being started without a positive confirmation st… | see DQ-WFI-001 | Tested | SAT-F-10 | Fail |
| URS-057 | Noise emitted by the system shall not exceed 80 dB(A) measured at one metre under nor… | see DQ-WFI-001 | Tested | — | — |
| URS-058 | The supplier shall provide, prior to Factory Acceptance Testing: general arrangement … | see DQ-WFI-001 | Tested | — | — |
| URS-059 | The supplier shall provide FAT and SAT protocols for user review and approval not les… | see DQ-WFI-001 | Deferred | — | Verified at SAT |
| URS-060 | The supplier shall provide IQ and OQ protocols and supporting documentation aligned w… | see DQ-WFI-001 | Deferred | SAT-I-14 | Fail |
| URS-061 | The supplier shall provide operation and maintenance manuals, a spare parts list with… | see DQ-WFI-001 | Tested | — | — |
| URS-062 | The supplier shall provide training for operators, maintenance personnel, and quality… | see DQ-WFI-001 | Deferred | SAT-F-20 | Fail |
| URS-063 | The system shall comply with the current USP and Ph. Eur. monographs for Water for In… | see DQ-WFI-001 | Deferred | — | Deferred again |
| URS-064 | WFI delivered at every point of use shall meet: conductivity in accordance with USP G… | see DQ-WFI-001 | Deferred | — | Deferred again |
| URS-065 | The system shall be designed, installed and qualified in accordance with EU GMP Annex… | see DQ-WFI-001 | Deferred | — | Deferred again |
| URS-066 | The control system shall comply with EU GMP Annex 11 and, where applicable to the sit… | see DQ-WFI-001 | Deferred | SAT-F-23 | Pass |
| URS-067 | The system shall be designed and documented in accordance with GAMP 5, and the suppli… | see DQ-WFI-001 | Tested | — | — |
| URS-068 | Equipment design shall follow ASME BPE for hygienic design, surface finish, fabricati… | see DQ-WFI-001 | Tested | — | — |
| URS-069 | The system shall support a three-phase Performance Qualification: Phase 1 with daily … | see DQ-WFI-001 | Deferred | — | Deferred again |
| URS-070 | Sample points shall be provided at the tank outlet, the loop supply, the loop return,… | see DQ-WFI-001 | Deferred | SAT-I-12 | Fail |
| URS-071 | Temperature mapping ports shall be provided at each worst-case location listed in App… | see DQ-WFI-001 | Deferred | SAT-I-13 | Fail |
| URS-072 | The supplier shall provide hydraulic calculations demonstrating that the minimum retu… | see DQ-WFI-001 | Deferred | — | Outstanding |
| URS-073 | Every requirement in this specification shall be traceable through design qualificati… | see DQ-WFI-001 | Deferred | — | Deferred again |
| URS-074 | The system shall permit challenge of the worst-case conditions listed in Appendix A d… | see DQ-WFI-001 | Deferred | — | Deferred again |

# Appendix B — Test Instruments Used

| Instrument | Used in | Required accuracy | Cal. cert / due |
| --- | --- | --- | --- |
| Digital level | SAT-I-03, SAT-I-05, SAT-F-18 | Accuracy 0.1 degrees or better |  |
| Boroscope | SAT-I-06, SAT-I-09 | Suitable for the smallest pipe bore in scope |  |
| Calibrated rule / calipers | SAT-I-07 | Resolution 1 mm or better |  |
| Torque wrench | SAT-I-03 | Accuracy 4% of reading or better |  |
| Tape measure | SAT-I-02, SAT-I-11 | Class II or better |  |
| Calibrated pressure gauges | SAT-I-04 | Accuracy 1% of span or better |  |
| Flow meter | SAT-F-05 | Accuracy 2% of reading or better |  |
| Signal simulator | SAT-F-24 | Accuracy 0.1% of span or better |  |
| Filter integrity tester | SAT-F-15 | Manufacturer specified for the filter type |  |
| UV inspection lamp | SAT-F-16 | 365 nm |  |

# Appendix C — As-Built Document Register

| Document | Number | Revision received | Date |
| --- | --- | --- | --- |
| P&ID | P&ID-005 | Rev C |  |
| As-built isometrics | ISO-011 | Rev B |  |
| General arrangement | GA-002 | Rev C |  |
| Electrical schematics | ELE-014 | Rev 4 |  |
| Instrument index | IDX-009 | Rev 2 |  |
| Weld log | WL-006 | As issued |  |
| Boroscopy record | BR-006 | As issued |  |
| Slope verification record | — | Not provided |  |
| Passivation certificate | PASS-041 | As issued |  |
| Material certificates | MTC pack | As issued |  |

As-built isometrics were received at Rev B. Three field routing changes are not reflected; see SDEV-011. Slope verification records for site-installed pipework were not provided; see SDEV-010.

# Appendix D — Software Configuration Recorded at Site

| Item | Version at FAT | Version at SAT |
| --- | --- | --- |
| PLC application | [From FAT-037] | Updated — duty rotation, audit trail, interlock |
| HMI application | [From FAT-037] | Updated — audit export, lockout indication |
| PLC firmware | [From FAT-037] | Unchanged |

Software was modified between Factory and Site Acceptance to close deviations DEV-006, DEV-007, DEV-009, DEV-010 and DEV-011. The change is recorded under site change control and the modified functions were retested at SAT-F-06 to SAT-F-11.

# Appendix E — Abbreviations

| Term | Definition |
| --- | --- |
| BMS | Building Management System |
| DQ | Design Qualification |
| DEV | FAT deviation |
| FAT | Factory Acceptance Test |
| HMI | Human Machine Interface |
| IQ | Installation Qualification |
| NTP | Network Time Protocol |
| OQ | Operational Qualification |
| P&ID | Piping and Instrumentation Diagram |
| POU | Point of use |
| PQ | Performance Qualification |
| SAT | Site Acceptance Test |
| SDEV | SAT deviation |
| SPL | SAT punch list item |
| URS | User Requirements Specification |
| VSR | Validation Summary Report |
| WFI | Water for Injection |